T H E   U N I V E R S I T Y   O F   N E W   S O U T H  W A L E S

[image: image1.png]il





P.O. BOX 1 -  KENSINGTON - NEW SOUTH WALES – AUSTRALIA - 2033

TELEX AA 26054 - TELEGRAPH: UNITECH SYDNEY - TELEPHONE 697 2222

EXTN

PLEASE QUOTE

SUMMARY OF TESTS ON INSULTEC MEMBRANE

CARRIED OUT AT THE UNIVERSITY OF NEW SOUTH WALES

Introduction


Prior to these tests it was claimed that, if the outside walls and roof of a building were coated with a novel membrane “Insultec”, then the interior of that building remained much cooler than a similar uncoated building or one coated with ordinary paint. Our purpose was to carry out tests under controlled conditions to ascertain the validity of the claim.

Nature of the tests:


A number of galvanized steel boxes of about 300mm cube size were constructed. Inside each box was placed an electronic thermometer, the output of which could be continually monitored. The boxes could be left bare or coated with various paints or membranes. The boxes were mounted on the roof of one of the University building in Kensington, New South Wales. The internal temperatures were recorded day and night for several days. The particular tests reported here compared two boxes coated with Insultec with a bare box over the period 30 June 1988 to 10 July 1988. The results refer to the times between 1100 hours and 1500 hours on all the days within that period when it was substantially sunny. It should be noted that even though it was winter, the uncoated box reached some 33 C on some occasions.

Results:


It was found that the boxes coated with Insultec remained of the order of 10 C cooler than the uncoated box when the sun was shining. The actual results are shown in the accompanying graph in which the temperature of the Insultec coated boxes is plotted against that of the uncoated box at the various times. Attention is drawn to the lines of best fit (for the two Insultec coated boxes) these show that the cooling benefit of the Insultec coating is always substantial but becomes even more so under warmer conditions. In other words we might expect a greater difference between the temperatures in the Insultec-coated and uncoated boxes during the summer. We have also obtained evidence that the temperature difference is greater for full size buildings than it is for the test boxes.

Conclusions:


It is concluded that the claims made for Insultec are fully justified. It is clear that this membrane acts as a heat rejecting medium and one can expect that, if the roof of a building is coated with Insultec, then the interior of that building will be 100 C or more cooler than that of a similar building with a plain galvanized roof during the warmest part of the day. 

[image: image2.png]



H.J. Goldsmid

Emeritus Professor of Physics

22 February 1990

Personal Profile

The testing program was performed under the supervision of Professor H.J. Goldsmid, Professor of Experimental Physics and Head of the Department of Applied Physics at the University of New South Wales. The following is a brief profile of Professor Goldsmid.

Qualifications:

B.Sc.Honours in Physics, Queen Mary College,




University of London




PhD University of London




D.Sc University of London




Fellow of the Australian Institute of Physics

Career


1951-1964

Staff of the Research Laboratories of the General Electric Co. 




Wembley England.




(Up to Principal Research Scientist)

1964 – 1969

Reader in Solid State Physics, University of New South Wales

1969 – 1988

Professor of Physics, University of New South Wales

1988 –present

Emeritus Professor Physics, Univ. New South Wales

1989-present

Chairman. National Standards Commission

Research Record
Author of about 150 publications, mainly in the field of thermo-




Electrics and thermal properties of materials, including thermal 




Conductivity. These include 6 textbooks.

Consultancies:
Consultant to the following organisations:




The General Electric Co. Ltd.




De La Rue Ltd.




AERE Harwell




IBM (UK) Ltd




Marlow Industries, Dallas, USA




Italian Atomic Energy Commission

UNIVERSITY OF NEW SOUTH WALES.

INSULTEC TEST – INTERNAL AIR SPACE

Taken over 19 sunny days in August – September 1989,

Shows plots of maximum temperature during the day

Measurements taken in the late afternoon.



[image: image3.wmf]Insultec Test - internal air space

10

15

20

25

30

17

19

21

23

25

27

29

31

2

4

6

8

10

12

14

16

18

20

22

24

Dates

Temperature C

GALVANISED IRON

FIBREGLASS BATTS

INSULTEC


_1097588831.xls
Chart1

		17		17		17

		19		19		19

		21		21		21

		23		23		23

		25		25		25

		27		27		27

		29		29		29

		31		31		31

		2		2		2

		4		4		4

		6		6		6

		8		8		8

		10		10		10

		12		12		12

		14		14		14

		16		16		16

		18		18		18

		20		20		20

		22		22		22

		24		24		24



GALVANISED IRON

FIBREGLASS BATTS

INSULTEC

Dates

Temperature C

Insultec Test - internal air space

27.7

22

19

29

22.5

20

28

22

18.8

27.5

22.5

19

26.8

18.8

17.3

27.5

24

21.4

20.5

17.5

12

25.5

21

15.3

26.7

21.4

17.2

25.8

20.8

17

26.5

20.8

17.4

30

23

18

17

12

10.3

27.43

20

16.8

30

20.8

18

29

18.9

17.2

27.2

23

20.5

26

22.8

20.3

26.5

22

19.2

28.5

22.8

20.3



Sheet1

				17		19		21		23		25		27		29		31		2		4		6		8		10		12		14		16		18		20		22		24

		GALVANISED IRON		27.7		29		28		27.5		26.8		27.5		20.5		25.5		26.7		25.8		26.5		30		17		27.43		30		29		27.2		26		26.5		28.5

		FIBREGLASS BATTS		22		22.5		22		22.5		18.8		24		17.5		21		21.4		20.8		20.8		23		12		20		20.8		18.9		23		22.8		22		22.8

		INSULTEC		19		20		18.8		19		17.3		21.4		12		15.3		17.2		17		17.4		18		10.3		16.8		18		17.2		20.5		20.3		19.2		20.3





Sheet2

		





Sheet3

		






