


[image: image1.png]



CZ52NS2830






        REPORT NO.:FNS0094

This report may only be reproduced in full

TESTS ON SPRAY APPLIED PAINT

 IN ACCORDANCE WITH BS 476: PART 7-1987

TRADE NAME 

INSULTEC

SPONSOR

SOLUX LIQUID INSULATION PTY LTD

30 Walker St WINDSOR NSW AUSTRALIA

DESCRIPTION
The sponsor described the sample as an high build re-radiating elastomeric

OF SAMPLE:
membrane. It is a water-based co-polymer compound containing pigments and fillers.

Two coats of the sample were applied over calcium silicate boards.


Nominal paint thickness:
250(m


Colour:



white

TEST METHOD:
The specimens were tested in accordance with British Standard 476, Fire tests on building materials and structures, Part 7. Method for classification of the surface spread of flame of products – 1987. For the test, each specimen measured 885 mm long and was clamped to the water-cooled frame

OBSERVATIONS:
The sample underwent blackening and blistering during the test.

	RESULTS:
	Specimen
	Spread of Flame

at 1.5 min (mm)
	Final spread of flame

at 10 min (mm)

	
	1
	*
	*

	
	2
	*
	*

	
	3
	*
	*

	
	4
	*
	*

	
	5
	*
	*

	
	6
	*
	*


* These samples did not ignite

CLASSIFICATION :
Class 1
 

The test results relate only to the behaviour of the test specimens of the  product under the particular conditions of test; they are not intended to be the sole criterion for assessing the potential fire hazard of the product in use.

DATE OF TEST: 
3 August 1999, Issued on the 4th day of August 1999 without alterations or additions.

[image: image2.png]



[image: image3.png]



 
[image: image4.png]LG e




Glenn Whittaker


Accreditation

Garry Collins

Testing Officer


No 3632

Manager, Fire Testing and Assessments

This laboratory is accredited by The National Association of Testing  Authorities, Australia. The tests reported herein have been performed in accordance with its terms of accreditation

[image: image5.png]Dmprnoving the Buill Environment



[image: image6.png]


 

Building, Construction and Engineering 

14 Julius Avenue, Riverside Corporate Park, Delhi Road, North Ryde NSW 2113 Australia

Telephone: 61 2 9490 5444 Facsimile: 61 2 9490 5655







